## Sheet1
NC No. | [5 empty] | Date |  |  |  | Inspector
Total Heating Surface | [6 empty] | Minimum Safety Relief Valve Capacity
Firebox |  | Firedoor Wall |  | Firebox TS |  | Tubes |  | Smokebox TS |  | Crownsheet |  | W=Width / H=Heigth
L |  | W |  | W |  | d |  | W |  | W |  | L=Length / A=Area / d=dia
H |  | H |  | H |  | L |  | H |  | L |  | HS=Heating Surface sqft
or |  |  |  | or |  | and |  | or |  |  |  | SF=Square feet / r=radius
d |  |  |  | d |  | No. |  | d |  |  |  | All measurments in inches
L
A) | Find the HS of the Firebox
| 1. Sides above the grates: |  |  |  |  | W * H * 2 / 144 = HS
| 0 | W * | 0 | H * | 2 | /144 | = |  |  |  |  | 0 | HS
| 2. Crown Sheet: |  |  |  |  | W * L / 144 = HS
| 0 | W * | 0 | L | /144 | = | [5 empty] | 0 | HS
| 3. Firedoor Wall: |  |  |  |  | W * H / 144 = HS
| 0 | W * | 0 | H | /144 | = | [5 empty] | 0 | HS
or
| 4. Round Firebox: |  |  |  |  | π * d * L / 144 = HS
| 3.1416 | * | 0 | d * | 0 | L / | 144 | = |  |  |  | 0 | HS
| 5. Firebox tubesheet: |  |  |  |  | W * H / 144 = HS
| 0 | W * | 0 | H | /144 | = |  |  | 0 | SF
| Minus Area of tube openings: | [6 empty] | π * r * r * No. Tubes / 144 = A
| 3.1416 | * | 0 | r* | 0 | r* | 0 | Tubes | = | 0 | A
| SF - A = Total HS of Firebox Tubesheet: | [10 empty] | 0 | HS
B) | Find the HS of the tubes: |  |  |  |  | 2*3.1416*r*L*No. Tubes / 144 = HS
2* | 3.1416 | * | 0 | r * | 0 | L * | 0 | No. Tubes |  | /144 | = | 0 | HS
C) | Find the area of the Smokebox tubesheet:
| Round: |  | 3.1416 * r * r / 144 - Area of tube openings = HS
| 3.1416 * | 0 | r * | 0 | r/144 | - | 0 | A = | 0 | HS
or
| Straight Sides: |  |  | W * H / 144 - Area of tube openings = HS
| 0 | W* | 0 | H / | 144 - | 0 | A = |  | 0 | HS
[12 empty] | 0 | HS
| Table S2.8.1 |  |  |  |  | TOTAL HEATING SURFACE | [5 empty] | 0 | HS
Boiler Heating Surface Firetube Boilers Watertube Boilers
| Hand-Fired 5 6 | [7 empty] | 0 | HS
| Stoker-Fired 7 8 | [6 empty] | X | 5 | Value from Table S2.8.1
| Power Burner 8 10 | [7 empty] | 0 | Minimum safety valve relief capacity
Hand-Fired Waterwall 8 8
Stoker Waterwall 10 12
Power Burner Waterwall 14 16